## 051 Cond Coil Coat
FIGURE G-1 ENERGY SAVINGS PROJECTION TOOL
Facility: | Your Facility Name
Capacity of HVAC Units
ECP Savings: | 371.6652 | Electric Demand kW |  |  | 461440.4614 | Electric Energy kWh
| 36915.2369 | Electric Energy Cost Savings |  |  | 1574.4349 | Electric Energy MMBtu
| -173187.834 | lbs of CO2 emissions |  |  | -503.8192 | lbs of NOx emissions
| -5.3531 | lbs of SO2 emissions
Total ECP Savings: | 36915.2369 | Total Annual Cost Savings |  |  | 1574.4349 | Total Annual MMBtu Savings
ECP Cost: | 165425
Payback: | 4.4812 | yrs (excluding maint savings)
Calculations
Assumptions: | This recommendation is applied in the following instances:
1) New equipment
2) Existing equipment with evidence of minor environmental damage
3) Equipment with five years of useful life remaining
The protective corrosion inhibitor is MicroGuard (TM) product from Adsil (TM)
Charlotte area has 1644 cooling degree days (CDD) per NOAA
Full-load equivalent operating hours = FLEOH= 0.8*CDD
Decrease in EER is assumed to be both an increase in power consumption
and capacity degradation
Savings to heat pumps during the heating season are not included
Average EER=9.0
Average EER gain =12.3%
Nominal capacity is total tonnage at facility. Available from equipment nameplate data.
May be estimated by taking total facility square footage and dividing by 400.
| CDD from website |  | http://lwf.ncdc.noaa.gov/oa/climate/online/ccd/nrmcdd.html
| 1644 | CDD | use website to get CDD for your city
| 1315.2 | FLEOH
| 0 | Demand Cost per kW
| 0.08 | Energy Cost per kWh |  |  | use blended electric rate
| 0.003412 | MMBtu/kWh
| 12.3% | EER gain | use default of 12.3% or value from degradation tool
HVAC System Data
Condensing Unit Data from: |  | SEQL Area |  |  |  | Nominal Capacity: | 2545 | tons
Condensing Unit Consumption: |  | 3393.3333 | kW |  |  | Present Condition EER: | 9 | Btu/W-hr
Calculated EER: |  | 10.107 | Btu/W-hr |  |  | kW/ton= | 1.3333
EER after coil application= |  | 10.107
kW/ton after coil application= |  | 1.1873
Demand Consumption= |  | 3021.6682
Facility: | Your Facility Name
Capacity of HVAC Units
Current Run-time Adjustment Factors
Night Setback: | 1 | Note 1 |  | Excess Capacity: |  | 1
FLEOH Conversion: | 0.8 |  |  | Weekend Setback: |  | 1 | Note 2
|  |  |  | Cooling Set Point: |  | 72 | Degrees F
Proposed Run-time Adjustment Factors
Night Setback: | 1 |  |  | Excess Capacity: |  | 1
FLEOH Conversion: | 0.8 |  |  | Weekend Setback: |  | 1
|  |  |  | Cooling Set Point: |  | 72 | Degrees F
Run-time Estimates
Current condensing unit: |  | 1241.5488 | hours - annually
Proposed condensing unit: |  | 1241.5488 | hours - annually
|  | kW |  | kWh
| Current | 3393.3333 |  | 4212988.928
| Proposed | 3021.6682 |  | 3751548.4666
| Savings | 371.6652 |  | 461440.4614
Installation Costs
Nominal capacity: |  |  |  | 2545 | tons
Cost associated to install coating (parts & labor): |  |  |  | 65 | per ton (total installed cost)
(vendor quotation)
| Total project cost: |  |  | 165425
Note 1: Use a night setback value of .95 if HAVC equipment does not run at night after 6:00 P.M. Use 1 if no
setback is used.
Note 2: Use a weekend setback value of .75 is HVAC is turned off for the weekend. Use .875 if it is turned off
for one day during the weekend.

## Emissions
Summary of power plant emissions savings associated with energy conservation measure*
| Pollutant type | Pollutant units: Lb/MMBTU | MMBTU Reduction from ECP | Yearly reduction in Pollutant (lbs.)
| CO2 | 110 | 1574.4349 | 173187.834
| SO2 | 0.0034 |  | 5.3531
| NOx | 0.32 |  | 503.8192
| 12.3% | EER gain | use default of 12.3% or value from degradation tool
0
Notes:
* In addition to the energy and cost savings associated with this ECP, the environmental benefits associated with a decrease in emissions based on AP-42 standards published by the EPA for Natural gas-fired turbines were also evaluated on an annual MMBTU decrease. The median pollution emitters (natural gas-fired turbines) emission factors were used to evaluate the reduction in pollutant emission. AP-42 standards published by the EPA for Natural gas-fired turbines can be found at the following EPA web sites, and may be used to more closely match the emissions in the area of your facility:
http://www.epa.gov/ttn/chief/ap42/
http://www.epa.gov/ttn/chief/ap42/ch03/final/c03s01.pdf
http://www.epa.gov/ttn/chief/ap42/ch03/final/c03s02.pdf