## Gen Data Entry
Enter Data in Blue Areas Only | Values entered in Blue area are for examples only. Update these.
A | B | C
TABLE 1 - GENERAL DATA ENTRY
POTW NAME: | Example
POTW HIGHEST MONTHLY AVERAGE FLOW (MGD): | 2.5
DOMESTIC FLOW (MGD): | 1.1
SIU FLOW (MGD): | 0.9
COMMERCIAL FLOW (MGD): | 0.5
TRUCKED AND HAULED WASTE FLOW (MGD): | 0.005
COMMERCIAL FLOW AS A % OF ALL NON-DOMESTIC | 35.9431
TOTAL COMMERCIAL FLOW AS A % OF TOTAL POTW FLOW | 20.2
TOTAL NON-DOMESTIC FLOW AS A % OF TOTAL POTW FLOW | 56.2
SPECIFIC GRAVITY OF SLUDGE TO DISPOSAL (kg/l) | 1 | Default 1 | See Appendix M of the Strategy
SLUDGE FLOW TO DISPOSAL (MGD): | 0.07
% SOLIDS TO DISPOSAL (%) | 3
BIOSOLIDS TABLE (1,3 OR "O"THER) BASED ON DISPOSAL OPTION: | 3
ARE YOU USING TABLE 2 FOR BIOSOLIDS (Y/N)?: | n
SITE AREA (ACRES): | 100
SITE LIFE (YEARS): | 100
CHRONIC RECEIVING WATER FLOW (MGD): | 6
ACUTE RECEIVING WATER FLOW (MGD): | 2
HARDNESS FOR METALS CALCULATIONS (MG/L): | 220
IS YOUR RECEIVING WATER A DRINKING WATER SUPPLY (Y/N)?: | Y
APPLICABLE STANDARDS (ACUTE, CHRONIC, BOTH): | B | A,C OR B

## Daily Criteria&Stds
Enter Data in Blue Areas Only
B | C | D | E | F | G | H | I
Daily
TABLE 2: CRITERIA AND STANDARDS | [5 empty] | OTHER CRITERIA
| Daily Max/7 Day | STATE | EPA ACUTE | FINAL
| NPDES PERMIT | ACUTE | H2O QUAL | ACUTE
| LIMITS | WQ STDS | CRITERIA | CRITERIA | MCLs
POLLUTANT | MG/L | MG/L | MG/L | MG/L | MG/L |  | POLLUTANT
ARSENIC |  | 0.34 |  | 0.34 | 0.01 |  | ARSENIC
CADMIUM | 0.024 | 0.018 | 0.0047548 | 0.018 | 0.005 |  | CADMIUM
CHROMIUM - TOTAL |  |  |  |  | 0.1 |  | CHROMIUM - TOTAL
CHROMIUM (III) |  | 1.708 | 3.4392 | 1.708 |  |  | CHROMIUM (III)
CHROMIUM (VI) | 0.022 | 0.016 | 0.016 | 0.016 |  |  | CHROMIUM (VI)
COPPER | 0.063 | 0.048 | 0.029426 | 0.048 | 1.3 |  | COPPER
LEAD |  | 0.268 | 0.22276 | 0.268 | 0.015 |  | LEAD
MERCURY |  | 1e-05 | 0.0024 | 1e-05 | 0.002 |  | MERCURY
MOLYBDENUM | [6 empty] | MOLYBDENUM
NICKEL |  | 1.455 | 0.91416 | 1.455 |  |  | NICKEL
SELENIUM | 0.023 | 0.018 | 0.02 | 0.018 | 0.05 |  | SELENIUM
SILVER | 0.027 | 0.02 | 0.014688 | 0.02 | 0.1 |  | SILVER
ZINC |  | 0.365 | 0.2337 | 0.365 | 5 |  | ZINC

## Mo Criteria&Stds
Enter Data in Blue Areas Only
B | C | D | E | F | G | H | I | J | K | L
Monthly
TABLE 3: CRITERIA AND STANDARDS | [8 empty] | OTHER CRITERIA
| Monthly | STATE | EPA CHRONIC | FINAL |  | STATE | EPA | Final
| NPDES PERMIT | CHRONIC | H2O QUAL | CHRONIC |  | HUMAN HEALTH | HUMAN HEALTH | HUMAN HEALTH | State
| LIMITS | WQ STDS | CRITERIA | CRITERIA |  | CRITERIA | CRITERIA | CRITERIA | Chronic Agriculture
POLLUTANT | MG/L | MG/L | MG/L | MG/L | POLLUTANT | MG/L | MG/L | MG/L | mg/l | POLLUTANT
ARSENIC |  | 0.1 |  | 0.1 | ARSENIC |  |  |  | 0.1 | ARSENIC
CADMIUM | 0.0092 | 0.006 | 0.00048536 | 0.006 | CADMIUM |  |  |  | 0.01 | CADMIUM
CHROMIUM - TOTAL |  |  |  |  | CHROMIUM - TOTAL |  |  |  |  | CHROMIUM - TOTAL
CHROMIUM (III) |  | 0.222 | 0.16438 | 0.222 | CHROMIUM (III) |  |  |  |  | CHROMIUM (III)
CHROMIUM (VI) | 0.017 | 0.011 | 0.011 | 0.011 | CHROMIUM (VI) |  |  |  |  | CHROMIUM (VI)
COPPER | 0.04 | 0.028 | 0.018299 | 0.028 | COPPER |  |  |  | 0.2 | COPPER
LEAD | 0.15 | 0.01 | 0.0086806 | 0.01 | LEAD |  |  |  | 0.1 | LEAD
MERCURY | 1.5e-05 | 1e-05 | 1.2e-05 | 1e-05 | MERCURY |  |  |  |  | MERCURY
MOLYBDENUM |  |  |  |  | MOLYBDENUM |  |  |  |  | MOLYBDENUM
NICKEL |  | 0.1621 | 0.10164 | 0.1621 | NICKEL | 4.6 |  | 4.6 | 0.2 | NICKEL
SELENIUM | 0.0055 | 0.0046 | 0.005 | 0.0046 | SELENIUM |  | 4.2 | 4.2 | 0.02 | SELENIUM
SILVER | 0.0049 | 0.0032 |  | 0.0032 | SILVER |  |  |  |  | SILVER
ZINC |  | 0.368 | 0.2337 | 0.368 | ZINC |  | 26 | 26 | 2 | ZINC

## INF&EFF
Enter Data in Blue Areas Only |  | THIS INFORMATION IS ONLY NECESSARY IF YOU ARE CALCULATING REMOVAL EFFICIENCY FROM POTW INF AND EFF DATA ONLY (See Rem Eff TABLE)
B | C | D | E | F | G | H | I | J | K
TABLE 4: INFLUENT AND EFFLUENT DATA
| AVERAGE | POTW |  |  | AVERAGE | POTW
| POTW | FLOW | COMMENT | POTW | POTW | FLOW | COMMENT | POTW
| INFLUENT |  | AND | INFLUENT | EFFLUENT |  | AND | EFFLUENT
POLLUTANT | MG/L | MGD | NOTES | LBS/DAY | MG/L | MGD | NOTES | LBS/DAY | POLLUTANT
ARSENIC |  | 2.2 | below detection |  |  | 2.2 | below detection |  | ARSENIC
CADMIUM | 0.002 | 2.2 |  | 0.036696 |  | 2.2 | below detection |  | CADMIUM
CHROMIUM - TOTAL | 0.06 | 2.2 |  | 1.1009 | 0.005 | 2.2 |  | 0.09174 | CHROMIUM - TOTAL
CHROMIUM (III) | 0.06 | 2.2 |  | 1.1009 | 0.003 | 2.2 |  | 0.055044 | CHROMIUM (III)
CHROMIUM (VI) | 0.005 | 2.2 |  | 0.09174 |  | 2.2 | below detection |  | CHROMIUM (VI)
COPPER | 0.1 | 2.2 |  | 1.8348 | 0.058 | 2.2 |  | 1.0642 | COPPER
LEAD | 0.01 | 2.2 |  | 0.18348 | 0.002 | 2.2 |  | 0.036696 | LEAD
MERCURY | 0.0003 | 2.2 |  | 0.0055044 |  | 2.2 | below detection (using 245.1) |  | MERCURY
MOLYBDENUM | 0.01 | 2.2 |  | 0.18348 | 0.002 | 2.2 |  | 0.036696 | MOLYBDENUM
NICKEL | 0.06 | 2.2 |  | 1.1009 | 0.009 | 2.2 |  | 0.16513 | NICKEL
SELENIUM |  | 2.2 | below detection |  |  | 2.2 | below detection |  | SELENIUM
SILVER | 0.032 | 2.2 |  | 0.58714 | 0.009 | 2.2 |  | 0.16513 | SILVER
ZINC | 0.12 | 2.2 |  | 2.2018 | 0.07 | 2.2 |  | 1.2844 | ZINC

## Dom, IU & Rec Water
Enter Data in Blue Areas Only
Purple Areas are Optional Data Entry Columns
B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R
TABLE 5: POLLUTANT LOADING AND RECEIVING WATER |  |  |  | USER ENTERED |  | FINAL |  |  |  | USER ENTERED |  |  |  | USER ENTERED
| TOTAL CURRENT |  | DOMESTIC | DOMESTIC |  | CALCULATED |  |  | COMMERCIAL | COMMERCIAL |  | CALCULATED | TOTAL DOMESTIC | TRUCKED AND | UPSTREAM
| SIU LOADING |  | CONTRIBUTION | LOADING |  | DOMESTIC |  |  | USER DISCHARGE | LOADING |  | COMMERCIAL | PLUS COMMERCIAL | HAULED WASTE | RECEIVING
| TO POTW |  | TO POTW | TO POTW |  | CONTRIBUTION |  |  | TO POTW | TO POTW |  | CONTRIBUTION | LOADING | LOADING TO POTW | WATER
POLLUTANT | LBS/D |  | MG/L | LBS/DAY |  | LBS/DAY | POLLUTANT |  | MG/L | LBS/DAY |  | LBS/DAY | LBS/D | LBS/DAY | MG/L | POLLUTANT
ARSENIC |  |  | 0.002 |  |  | 0.018348 | ARSENIC |  | 0.007 |  |  | 0.02919 | 0.047538 |  |  | ARSENIC
CADMIUM |  |  | 0.001 |  |  | 0.009174 | CADMIUM |  | 0.02 |  |  | 0.0834 | 0.092574 |  |  | CADMIUM
CHROMIUM - TOTAL |  |  | 0.0029 |  |  | 0.026605 | CHROMIUM - TOTAL |  | 0.1 |  |  | 0.417 | 0.4436 |  |  | CHROMIUM - TOTAL
CHROMIUM (III) | [5 empty] | Need Domestic Data | CHROMIUM (III) |  |  |  |  | Need Commercial Data | Dom or Comm Data Missing |  |  | CHROMIUM (III)
CHROMIUM (VI) |  |  | 0.005 |  |  | 0.04587 | CHROMIUM (VI) |  | 0.001 |  |  | 0.00417 | 0.05004 |  |  | CHROMIUM (VI)
COPPER |  |  | 0.058 |  |  | 0.53209 | COPPER |  | 0.06 |  |  | 0.2502 | 0.78229 |  |  | COPPER
LEAD |  |  | 0.001 |  |  | 0.009174 | LEAD |  | 0.003 |  |  | 0.01251 | 0.021684 |  |  | LEAD
MERCURY |  |  | 0.0003 |  |  | 0.0027522 | MERCURY |  | 0.0005 |  |  | 0.002085 | 0.0048372 |  |  | MERCURY
MOLYBDENUM |  |  | 0.003 |  |  | 0.027522 | MOLYBDENUM |  | 0.05 |  |  | 0.2085 | 0.23602 |  |  | MOLYBDENUM
NICKEL |  |  | 0.005 |  |  | 0.04587 | NICKEL |  | 0.03 |  |  | 0.1251 | 0.17097 |  |  | NICKEL
SELENIUM |  |  | 0.3 |  |  | 2.7522 | SELENIUM |  | 0.3 |  |  | 1.251 | 4.0032 |  |  | SELENIUM
SILVER |  |  | 0.002 |  |  | 0.018348 | SILVER |  | 0.06 |  |  | 0.2502 | 0.26855 |  |  | SILVER
ZINC |  |  | 0.102 |  |  | 0.93575 | ZINC |  | 0.112 |  |  | 0.46704 | 1.4028 |  |  | ZINC

## Biosolids
Enter Data in Blue Areas Only
B | C | D | E | F | G | H | I | J
|  | TABLE 1 | TABLE 3 | TABLE 2 | TABLE 2 | ENTER
TABLE 6: BIOSOLIDS | POTW | MAXIMUM | "CLEAN" | (CAR) | CALC. | DEFAULT | FINAL
| BIOSOLIDS TO | LAND APP | LAND APP | CUMULATIVE | SLUDGE | BIOSOLIDS | SLUDGE
| DISPOSAL | SLUDGE | SLUDGE | APPLICATION | DISPOSAL | DISPOSAL | CRITERIA
| MG/KG | CRITERIA | CRITERIA | RATE | CRITERIA | CRITERIA
POLLUTANT | DRY WT. | MG/KG | MG/KG | LBS/ACRE | MG/KG | MG/KG | MG/KG | POLLUTANT
ARSENIC | 1.6 |  | 41 |  |  |  | 41 | ARSENIC
CADMIUM | 2.1 |  | 39 |  |  |  | 39 | CADMIUM
CHROMIUM - TOTAL | 19.3 |  |  |  |  | 820 | 820 | CHROMIUM - TOTAL
CHROMIUM (III) | [6 empty] | No Criteria | CHROMIUM (III)
CHROMIUM (VI) | [6 empty] | No Criteria | CHROMIUM (VI)
COPPER | 457 |  | 1500 |  |  |  | 1500 | COPPER
LEAD | 48.6 |  | 300 |  |  |  | 300 | LEAD
MERCURY | 2.3 |  | 17 |  |  |  | 17 | MERCURY
MOLYBDENUM | 8.5 |  | 75 |  |  |  | 75 | MOLYBDENUM
NICKEL | 14.6 |  | 420 |  |  |  | 420 | NICKEL
SELENIUM | 7.3 |  | 100 |  |  |  | 100 | SELENIUM
SILVER | 37.2 |  |  |  |  | 121 | 121 | SILVER
ZINC | 820 |  | 2800 |  |  |  | 2800 | ZINC

## Rem Eff
Enter Data in Blue Areas Only
Purple Areas are Optional Data Entry Columns
B | C | D | E | F | G | H | I | J | K | L | M | N | O
[7 empty] | ENTER THE NAME |  | USER
TABLE 7: REMOVAL EFFICIENCY CALCULATIONS | INFEFF | ADRE | MRE | DECILE | LIT |  | OF THE REMOVAL |  | ENTERED | USE
| Influent/Effluent Method | ADRE METHOD | MRE METHOD | DECILE METHOD | LITERATURE | SOURCE OF | EFFICIENCY TO BE |  | SLUDGE | SLUDGE |  | FINAL
Removal Efficiencies must be 1-99% | Removal | REMOVAL | REMOVAL | REMOVAL | REMOVAL | LITERATURE | USED: INFEFF, ADRE, MRE, |  | REMOVAL | REMOVAL |  | POTW
| Efficiency | EFFICIENCY | EFFICIENCY | EFFICIENCY | EFFICIENCY | REMOVAL EFFICIENCY | DECILE, OR LIT |  | EFFICIENCY | EFFICIENCY? |  | REMOVAL
POLLUTANT | % | % | % | % | % | DATA |  |  | % | Y/N |  | % | POLLUTANT
ARSENIC | Influent-Effluent Data Prevents Reff Calc |  |  |  | 49 | EPA | LIT |  |  | N |  | 49 | ARSENIC
CADMIUM | Influent-Effluent Data Prevents Reff Calc |  |  |  | 64 | EPA | LIT |  |  | N |  | 64 | CADMIUM
CHROMIUM - TOTAL | 91.6667 | [5 empty] | INFEFF |  |  | N |  | 91.6667 | CHROMIUM - TOTAL
CHROMIUM (III) | 95 | [5 empty] | INFEFF |  |  | N |  | 95 | CHROMIUM (III)
CHROMIUM (VI) | Influent-Effluent Data Prevents Reff Calc |  |  |  | 82 | ACTIVATED SLUDGE | LIT |  |  | N |  | 82 | CHROMIUM (VI)
COPPER | 42 | 62 | 63 | 62 |  |  | INFEFF |  |  | N |  | 42 | COPPER
LEAD | 80 | 79 | 87 | 87 |  |  | INFEFF |  |  | N |  | 80 | LEAD
MERCURY | Influent-Effluent Data Prevents Reff Calc |  |  |  | 85 | TULSA WWTP | LIT |  |  | N |  | 85 | MERCURY
MOLYBDENUM | 80 | [5 empty] | INFEFF |  |  | N |  | 80 | MOLYBDENUM
NICKEL | 85 | [5 empty] | INFEFF |  |  | N |  | 85 | NICKEL
SELENIUM | Influent-Effluent Data Prevents Reff Calc |  |  |  | 48 | EPA | LIT |  |  | N |  | 48 | SELENIUM
SILVER | 71.875 | 56 | 60 | 58 |  |  | INFEFF |  |  | N |  | 71.875 | SILVER
ZINC | 41.6667 | 61 | 61 | 62 |  |  | INFEFF |  |  | N |  | 41.6667 | ZINC

## Daily MAHL Calcs
Enter Data in Blue Areas Only
B | C | D | E | F | G | H | I
DAILY |  |  |  | OTHER CRITERIA
TABLE 8: MAHL CALCULATIONS |  |  |  | FROM Daily Criteria&Stds |  | NAME OF
| Daily/7 day |  |  | COLUMN H | MOST | MAHL
| NPDES | ACUTE | LOADING |  | STRINGENT | FOR DAILY MAX
| LOADING | LOADING | FOR MCL |  | CRITERIA | LIMITS
POLLUTANT | LBS/DAY | LBS/DAY | LBS/DAY |  | LBS/DAY |  | POLLUTANT
ARSENIC | 999999 | 25.02 | 1.39 | 999999 | 1.39 | MCL | ARSENIC
CADMIUM | 1.39 | 1.8765 | 0.98458 | 999999 | 0.98458 | MCL | CADMIUM
CHROMIUM - TOTAL | 999999 | 999999 | 85.068 | 999999 | 85.068 | MCL | CHROMIUM - TOTAL
CHROMIUM (III) | 999999 | 1282.0248 | 999999 | 999999 | 1282.0248 | WQ-ACUTE | CHROMIUM (III)
CHROMIUM (VI) | 2.5483 | 3.336 | 999999 | 999999 | 2.5483 | NPDES Daily | CHROMIUM (VI)
COPPER | 2.2647 | 3.1059 | 158.8914 | 999999 | 2.2647 | NPDES Daily | COPPER
LEAD | 999999 | 50.2902 | 5.3167 | 999999 | 5.3167 | MCL | LEAD
MERCURY | 999999 | 0.002502 | 0.9452 | 999999 | 0.002502 | WQ-ACUTE | MERCURY
MOLYBDENUM | 999999 | 999999 | 999999 | 999999 | No Criteria | No Criteria | MOLYBDENUM
NICKEL | 999999 | 364.041 | 999999 | 999999 | 364.041 | WQ-ACUTE | NICKEL
SELENIUM | 0.92221 | 1.2991 | 6.8163 | 999999 | 0.92221 | NPDES Daily | SELENIUM
SILVER | 2.0016 | 2.6688 | 25.2053 | 999999 | 2.0016 | NPDES Daily | SILVER
ZINC | 999999 | 23.4831 | 607.6286 | 999999 | 23.4831 | WQ-ACUTE | ZINC

## Mo MAHL Calcs
Enter Data in Blue Areas Only
B | C | D | E | F | G | H | I | J
MONTHLY |  |  |  | OTHER CRITIERIA
TABLE 9: MAHL CALCULATIONS |  |  |  | FROM Mo Criteria&Stds | TABLE 1, 2, 3 OR |  | NAME OF
| Monthly | CHRONIC | LOADING | Column K | OTHER | MOST | MAHL
| NPDES | Toxicity | FOR HUMAN | State | SLUDGE | STRINGENT | For
| LOADING | Loading | HEALTH | Chronic Agriculture | LOADING | CRITERIA | Monthly
POLLUTANT | LBS/DAY | LBS/DAY | LBS/DAY | mg/l | LBS/DAY | LBS/DAY | Limits | POLLUTANT
ARSENIC | 999999 | 13.9 | 999999 | 13.9 | 1.4655 | 1.4655 | Biosolids | ARSENIC
CADMIUM | 0.53283 | 1.1815 | 999999 | 1.9692 | 1.0673 | 0.53283 | NPDES Monthly | CADMIUM
CHROMIUM - TOTAL | 999999 | 999999 | 999999 | 999999 | 15.6671 | 15.6671 | Biosolids | CHROMIUM - TOTAL
CHROMIUM (III) | 999999 | 314.7516 | 999999 | 999999 | 999999 | 314.7516 | WQ-CHRONIC | CHROMIUM (III)
CHROMIUM (VI) | 1.9692 | 4.3322 | 999999 | 999999 | 999999 | 1.9692 | NPDES Monthly | CHROMIUM (VI)
COPPER | 1.4379 | 3.4223 | 999999 | 24.4448 | 62.55 | 1.4379 | NPDES Monthly | COPPER
LEAD | 15.6375 | 3.5445 | 999999 | 35.445 | 6.5678 | 3.5445 | WQ-CHRONIC | LEAD
MERCURY | 0.002085 | 0.004726 | 999999 | 999999 | 0.35028 | 0.002085 | NPDES Monthly | MERCURY
MOLYBDENUM | 999999 | 999999 | 999999 | 999999 | 1.6419 | 1.6419 | Biosolids | MOLYBDENUM
NICKEL | 999999 | 76.6085 | 2173.96 | 94.52 | 8.654 | 8.654 | Biosolids | NICKEL
SELENIUM | 0.22053 | 0.6271 | 572.5731 | 2.7265 | 3.6488 | 0.22053 | NPDES Monthly | SELENIUM
SILVER | 0.36325 | 0.80657 | 999999 | 999999 | 2.9484 | 0.36325 | NPDES Monthly | SILVER
ZINC | 999999 | 44.7215 | 3159.6686 | 243.0514 | 117.6941 | 44.7215 | WQ-CHRONIC | ZINC

## Daily Only LL
Enter Data in Blue Areas Only
B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U
[13 empty] | If you are adopting | If setting | Percentage | MACL | MAIL
TABLE 10: DAILY LOCAL LIMITS |  |  |  | SAFETY/ | MAHL WITH | ENTER "Y" FOR | [6 empty] | a Commercial Limit, | SIU and Commercial limits | of MAL that |  |  | CALCULATED
|  | FINAL |  | EXPANSION | SAFETY - | for a SIU and a | MAHL minus | Maximum |  | MASS |  |  | then these are the | Enter % of MAL to | will be | Calculated | Calculated | UNIFORM
| Most | MAHL FOR |  | FACTOR % | EXPANSION | Commercial Limit | DOM + COM | Allowable Load |  | RESERVED | MAL |  | loadings from | allocate to SIUs | allocated to | ALLOCATION | ALLOCATION | LOCAL LIMITS
| Stringent | Daily | Name | FOR DAILY | FACTOR | ENTER A "N" FOR | LOADING | MAL |  | FOR HAULED | MINUS THE HAULED WASTE |  | Table 5 | Enter 100% if no Commercial Limit | Commercial Users | FOR COMMERCIAL | FOR SIUs | FOR SIUs
POLLUTANT | MAHL | LOCAL LIMITS | FOR MAHL | MAX LIMITS | LBS/DAY | SIU Limit Only | LBS/DAY | LBS/DAY | MAL is for | WASTE lbs/d | LBS/DAY | POLLUTANT | lbs/day | % | % | LBS/DAY | LBS/DAY | MG/L | POLLUTANT
ARSENIC | 1.39 | 1.39 | MCL | 10 | 1.251 | y | 1.2327 | 1.2327 | Commercial + SIUs |  | 1.2327 | ARSENIC | 0.02919 |  | Enter a % in Column P | #VALUE! | Enter a % in Column P | Enter a % in Column P | ARSENIC
CADMIUM | 0.53283 | 0.53283 | NPDES Monthly | 10 | 0.47955 | y | 0.47038 | 0.47038 | Commercial + SIUs |  | 0.47038 | CADMIUM | 0.0834 | 30 | 70 | 0.32926 | 0.14111 | 0.018854 | CADMIUM
CHROMIUM - TOTAL | 15.6671 | 15.6671 | Biosolids | 10 | 14.1004 | y | 14.0738 | 14.0738 | Commercial + SIUs |  | 14.0738 | CHROMIUM - TOTAL | 0.417 | 20 | 80 | 11.259 | 2.8148 | 0.37608 | CHROMIUM - TOTAL
CHROMIUM (III) | 314.7516 | 314.7516 | WQ-CHRONIC | 10 | 283.2764 | y | Dom or Comm Data Missing | Dom or Comm Data Missing | Commercial + SIUs |  | Dom or Comm Data Missing | CHROMIUM (III) | Need Commercial Data | 30 | 70 | Dom or Comm Data Missing | Dom or Comm Data Missing | Dom or Comm Data Missing | CHROMIUM (III)
CHROMIUM (VI) | 1.9692 | 1.9692 | NPDES Monthly | 10 | 1.7723 | y | 1.7264 | 1.7264 | Commercial + SIUs |  | 1.7264 | CHROMIUM (VI) | 0.00417 | 30 | 70 | 1.2085 | 0.51791 | 0.069199 | CHROMIUM (VI)
COPPER | 1.4379 | 1.4379 | NPDES Monthly | 10 | 1.2941 | y | 0.76205 | 0.76205 | Commercial + SIUs |  | 0.76205 | COPPER | 0.2502 | 30 | 70 | 0.53343 | 0.22861 | 0.030545 | COPPER
LEAD | 3.5445 | 3.5445 | WQ-CHRONIC | 10 | 3.19 | y | 3.1809 | 3.1809 | Commercial + SIUs |  | 3.1809 | LEAD | 0.01251 | 20 | 80 | 2.5447 | 0.63618 | 0.085 | LEAD
MERCURY | 0.002085 | 0.002085 | NPDES Monthly | 10 | 0.0018765 | y | 0 Discharge | 0 Discharge | Commercial + SIUs |  | 0 Discharge | MERCURY | 0.002085 | 5 | 95 | 0 Discharge | 0 Discharge | 0 Discharge | MERCURY
MOLYBDENUM | 1.6419 | 1.6419 | Biosolids | 10 | 1.4777 | y | 1.4502 | 1.4502 | Commercial + SIUs |  | 1.4502 | MOLYBDENUM | 0.2085 | 30 | 70 | 1.0152 | 0.43507 | 0.05813 | MOLYBDENUM
NICKEL | 8.654 | 8.654 | Biosolids | 10 | 7.7886 | y | 7.7427 | 7.7427 | Commercial + SIUs |  | 7.7427 | NICKEL | 0.1251 | 30 | 70 | 5.4199 | 2.3228 | 0.31035 | NICKEL
SELENIUM | 0.22053 | 0.22053 | NPDES Monthly | 10 | 0.19848 | y | 0 Discharge | 0 Discharge | Commercial + SIUs |  | 0 Discharge | SELENIUM | 1.251 | 20 | 80 | 0 Discharge | 0 Discharge | 0 Discharge | SELENIUM
SILVER | 0.36325 | 0.36325 | NPDES Monthly | 10 | 0.32693 | y | 0.30858 | 0.30858 | Commercial + SIUs |  | 0.30858 | SILVER | 0.2502 | 25 | 75 | 0.23144 | 0.077145 | 0.010307 | SILVER
ZINC | 23.4831 | 23.4831 | WQ-ACUTE | 10 | 21.1348 | y | 20.199 | 20.199 | Commercial + SIUs |  | 20.199 | ZINC | 0.46704 | 30 | 70 | 14.1393 | 6.0597 | 0.80964 | ZINC
Commercial + SIUs
SIUs

## Daily Only LL Summary
Enter Data in Blue Areas Only
B | C | D | E | F | G | H
MOST STRINGENT OF DAILY AND MONTHLY
TABLE 11: Daily LOCAL LIMIT SUMMARY | DAILY AVERAGE LOCAL LIMIT INFORMATION
| MAIL | UNIFORM | MACL | PROPOSED | PROPOSED
| FOR SIUs | CONCENTRATION | FOR COMMERCIAL | DAILY MAXIMUM | MACL FOR
POLLUTANT | LBS/DAY | FOR SIUs (MG/L) | USERS (LBS/DAY) | LIMIT | COMMERCIAL USERS | POLLUTANT
ARSENIC | Enter a % in Column P | Enter a % in Column P | #VALUE! |  |  | ARSENIC
CADMIUM | 0.14111 | 0.018854 | 0.32926 |  |  | CADMIUM
CHROMIUM - TOTAL | 2.8148 | 0.37608 | 11.259 |  |  | CHROMIUM - TOTAL
CHROMIUM (III) | Dom or Comm Data Missing | Dom or Comm Data Missing | Dom or Comm Data Missing |  |  | CHROMIUM (III)
CHROMIUM (VI) | 0.51791 | 0.069199 | 1.2085 |  |  | CHROMIUM (VI)
COPPER | 0.22861 | 0.030545 | 0.53343 |  |  | COPPER
LEAD | 0.63618 | 0.085 | 2.5447 |  |  | LEAD
MERCURY | 0 Discharge | 0 Discharge | 0 Discharge |  |  | MERCURY
MOLYBDENUM | 0.43507 | 0.05813 | 1.0152 |  |  | MOLYBDENUM
NICKEL | 2.3228 | 0.31035 | 5.4199 |  |  | NICKEL
SELENIUM | 0 Discharge | 0 Discharge | 0 Discharge |  |  | SELENIUM
SILVER | 0.077145 | 0.010307 | 0.23144 |  |  | SILVER
ZINC | 6.0597 | 0.80964 | 14.1393 |  |  | ZINC

## Notes to User
The following tables are where you intend to set Daily and Monthly Local Limits
If you are intending to set Daily limits only, use the previous 2 tables.

## Daily AND Mo LL
Enter Data in Blue Areas Only
B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U
[13 empty] | If you are adopting | If setting | Percentage | MACL | MAIL
TABLE 12: DAILY LOCAL LIMITS |  |  |  | SAFETY/ | MAHL WITH | ENTER "Y" FOR | [6 empty] | a Commercial Limit, | SIU and Commercial limits | of MAL that |  |  | CALCULATED
where also calc monthly |  | FINAL |  | EXPANSION | SAFETY - | for a SIU and a | MAHL minus | Maximum |  | MASS |  |  | then these are the | Enter % of MAL to | will be | Calculated | Calculated | UNIFORM
|  | MAHL FOR |  | FACTOR % | EXPANSION | Commercial Limit | DOM + COM | Allowable Load |  | RESERVED | MAL |  | loadings from | allocate to SIUs | allocated to | ALLOCATION | ALLOCATION | LOCAL LIMITS
|  | DAILY | Name | FOR DAILY | FACTOR | ENTER A "N" FOR | LOADING | MAL |  | FOR HAULED | MINUS THE HAULED WASTE |  | Table 5 | Enter 100% if no Commercial Limit | Commercial Users | FOR COMMERCIAL | FOR SIUs | FOR SIUs
POLLUTANT | Daily MAHL | LOCAL LIMITS | FOR MAHL | MAX LIMITS | LBS/DAY | SIU Limit Only | LBS/DAY | LBS/DAY | MAL is for | WASTE lbs/d | LBS/DAY | POLLUTANT | lbs/day | % | % | LBS/DAY | LBS/DAY | MG/L | POLLUTANT
ARSENIC | 1.39 | 1.39 | MCL | 10 | 1.251 | y | 1.2327 | 1.2327 | Commercial+SIUs |  | 1.2327 | ARSENIC | 0.02919 |  | Enter a % in Column P | #VALUE! | Enter a % in Column P | Enter a % in Column P | ARSENIC
CADMIUM | 0.98458 | 0.98458 | MCL | 10 | 0.88613 | y | 0.87695 | 0.87695 | Commercial+SIUs |  | 0.87695 | CADMIUM | 0.0834 | 20 | 80 | 0.70156 | 0.17539 | 0.023434 | CADMIUM
CHROMIUM - TOTAL | 85.068 | 85.068 | MCL | 10 | 76.5612 | y | 76.5346 | 76.5346 | Commercial+SIUs |  | 76.5346 | CHROMIUM - TOTAL | 0.417 | 33 | 67 | 51.2782 | 25.2564 | 3.3745 | CHROMIUM - TOTAL
CHROMIUM (III) | 1282.0248 | 1282.0248 | WQ-ACUTE | 10 | 1153.8223 | y | Dom or Comm Data Missing | Dom or Comm Data Missing | Commercial+SIUs |  | Dom or Comm Data Missing | CHROMIUM (III) | Need Commercial Data | 15 | 85 | Dom or Comm Data Missing | Dom or Comm Data Missing | Dom or Comm Data Missing | CHROMIUM (III)
CHROMIUM (VI) | 2.5483 | 2.5483 | NPDES Daily | 10 | 2.2935 | y | 2.2476 | 2.2476 | Commercial+SIUs |  | 2.2476 | CHROMIUM (VI) | 0.00417 | 15 | 85 | 1.9105 | 0.33714 | 0.045046 | CHROMIUM (VI)
COPPER | 2.2647 | 2.2647 | NPDES Daily | 10 | 2.0383 | y | 1.5062 | 1.5062 | Commercial+SIUs |  | 1.5062 | COPPER | 0.2502 | 25 | 75 | 1.1296 | 0.37654 | 0.05031 | COPPER
LEAD | 5.3167 | 5.3167 | MCL | 10 | 4.7851 | y | 4.7759 | 4.7759 | Commercial+SIUs |  | 4.7759 | LEAD | 0.01251 | 10 | 90 | 4.2983 | 0.47759 | 0.063811 | LEAD
MERCURY | 0.002502 | 0.002502 | WQ-ACUTE | 10 | 0.0022518 | y | 0 Discharge | 0 Discharge | Commercial+SIUs |  | 0 Discharge | MERCURY | 0.002085 | 5 | 95 | 0 Discharge | 0 Discharge | 0 Discharge | MERCURY
MOLYBDENUM | No Criteria | No Criteria | No Criteria | 10 | No Criteria | y | No Criteria | No Criteria | Commercial+SIUs |  | No Criteria | MOLYBDENUM | 0.2085 | 10 | 90 | No Criteria | No Criteria | No Criteria | MOLYBDENUM
NICKEL | 364.041 | 364.041 | WQ-ACUTE | 10 | 327.6369 | y | 327.591 | 327.591 | Commercial+SIUs |  | 327.591 | NICKEL | 0.1251 | 22 | 78 | 255.521 | 72.07 | 9.6294 | NICKEL
SELENIUM | 0.92221 | 0.92221 | NPDES Daily | 10 | 0.82999 | y | 0 Discharge | 0 Discharge | Commercial+SIUs |  | 0 Discharge | SELENIUM | 1.251 | 10 | 90 | 0 Discharge | 0 Discharge | 0 Discharge | SELENIUM
SILVER | 2.0016 | 2.0016 | NPDES Daily | 10 | 1.8014 | y | 1.7831 | 1.7831 | Commercial+SIUs |  | 1.7831 | SILVER | 0.2502 | 15 | 85 | 1.5156 | 0.26746 | 0.035736 | SILVER
ZINC | 23.4831 | 23.4831 | WQ-ACUTE | 10 | 21.1348 | y | 20.199 | 20.199 | Commercial+SIUs |  | 20.199 | ZINC | 0.46704 | 15 | 85 | 17.1692 | 3.0299 | 0.40482 | ZINC
Commercial+SIUs
SIUs

## Mo AND Daily LL
Enter Data in Blue Areas Only
B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S
[11 empty] | If you are adopting |  | Percentage
TABLE 13: MONTHLY LOCAL LIMITS |  |  |  | SAFETY/ | MAHL WITH | ENTER "Y" FOR |  |  |  |  | a Commercial Limit, | Percentage of | of MAL that | MACL | MAIL | CALCULATED
|  | FINAL |  | EXPANSION | SAFETY - | for a SIU and a | MAHL minus | Maximum |  |  | then these are the | MAL to | will be | Calculated | Calculated | UNIFORM
|  | MAHL FOR | NAME FROM | FACTOR % | EXPANSION | Commercial Limit | DOM + COM | Allowable Load |  |  | loadings from | allocate to | allocated to | ALLOCATION | ALLOCATION | LOCAL LIMITS
|  | DAILY | TABLE 6 | FOR DAILY | FACTOR | ENTER A "N" FOR | LOADING | MAL |  |  | Table 5 | SIUs Only | Commercial Users | FOR COMMERCIAL | FOR SIUs | FOR SIUs
POLLUTANT | MONTHLY MAHL | LOCAL LIMITS | FOR MAHL | MAX LIMITS | LBS/DAY | SIU Limit Only | LBS/DAY | LBS/DAY | MAL is for | POLLUTANT | lbs/day | % | % | LBS/DAY | LBS/DAY | MG/L | POLLUTANT
ARSENIC | 1.4655 | 1.4655 | Biosolids | 10 | 1.3189 | Y | 1.3006 | 1.3006 | Commercial+SIUs | ARSENIC | 0.02919 |  | Enter a % in Column N | #VALUE! | Enter a % in Column N | Enter a % in Column N | ARSENIC
CADMIUM | 0.53283 | 0.53283 | NPDES Monthly | 10 | 0.47955 | Y | 0.47038 | 0.47038 | Commercial+SIUs | CADMIUM | 0.0834 | 30 | 70 | 0.32926 | 0.14111 | 0.018854 | CADMIUM
CHROMIUM - TOTAL | 15.6671 | 15.6671 | Biosolids | 10 | 14.1004 | y | 14.0738 | 14.0738 | Commercial+SIUs | CHROMIUM - TOTAL | 0.417 | 20 | 80 | 11.259 | 2.8148 | 0.37608 | CHROMIUM - TOTAL
CHROMIUM (III) | 314.7516 | 314.7516 | WQ-CHRONIC | 10 | 283.2764 | y | Dom or Comm Data Missing | Dom or Comm Data Missing | Commercial+SIUs | CHROMIUM (III) | Need Commercial Data | 15 | 85 | Dom or Comm Data Missing | Dom or Comm Data Missing | Dom or Comm Data Missing | CHROMIUM (III)
CHROMIUM (VI) | 1.9692 | 1.9692 | NPDES Monthly | 10 | 1.7723 | y | 1.7264 | 1.7264 | Commercial+SIUs | CHROMIUM (VI) | 0.00417 | 17 | 83 | 1.4329 | 0.29348 | 0.039213 | CHROMIUM (VI)
COPPER | 1.4379 | 1.4379 | NPDES Monthly | 10 | 1.2941 | y | 0.76205 | 0.76205 | Commercial+SIUs | COPPER | 0.2502 | 22 | 78 | 0.5944 | 0.16765 | 0.0224 | COPPER
LEAD | 3.5445 | 3.5445 | WQ-CHRONIC | 10 | 3.19 | y | 3.1809 | 3.1809 | Commercial+SIUs | LEAD | 0.01251 | 15 | 85 | 2.7037 | 0.47713 | 0.06375 | LEAD
MERCURY | 0.002085 | 0.002085 | NPDES Monthly | 10 | 0.0018765 | y | 0 Discharge | 0 Discharge | Commercial+SIUs | MERCURY | 0.002085 | 5 | 95 | 0 Discharge | 0 Discharge | 0 Discharge | MERCURY
MOLYBDENUM | 1.6419 | 1.6419 | Biosolids | 10 | 1.4777 | y | 1.4502 | 1.4502 | Commercial+SIUs | MOLYBDENUM | 0.2085 | 20 | 80 | 1.1602 | 0.29004 | 0.038753 | MOLYBDENUM
NICKEL | 8.654 | 8.654 | Biosolids | 10 | 7.7886 | y | 7.7427 | 7.7427 | Commercial+SIUs | NICKEL | 0.1251 | 20 | 80 | 6.1942 | 1.5485 | 0.2069 | NICKEL
SELENIUM | 0.22053 | 0.22053 | NPDES Monthly | 10 | 0.19848 | y | 0 Discharge | 0 Discharge | Commercial+SIUs | SELENIUM | 1.251 | 10 | 90 | 0 Discharge | 0 Discharge | 0 Discharge | SELENIUM
SILVER | 0.36325 | 0.36325 | NPDES Monthly | 10 | 0.32693 | y | 0.30858 | 0.30858 | Commercial+SIUs | SILVER | 0.2502 | 31 | 69 | 0.21292 | 0.09566 | 0.012781 | SILVER
ZINC | 44.7215 | 44.7215 | WQ-CHRONIC | 10 | 40.2493 | y | 39.3136 | 39.3136 | Commercial+SIUs | ZINC | 0.46704 | 20 | 80 | 31.4509 | 7.8627 | 1.0505 | ZINC
Commercial+SIUs
SIUs

## Mo-Daily LL Summary
Enter Data in Blue Areas Only
USE COLUMNS C-G, IF YOU ARE SETTING DAILY AND MONTHLY LIMITS
USE COLUMNS I-M, IF YOU ARE SETTING DAILY AND MONTHLY LIMITS
B | C | D | E | F | G | H | I | J | K | L | M | N
TABLE 14: LOCAL LIMIT SUMMARY | DAILY MAXIUM LOCAL LIMIT INFORMATION | [5 empty] | MONTHLY AVERAGE LOCAL LIMIT INFORMATION
FOR DAILY AND MONTHLY LL | MAIL | UNIFORM | MACL | PROPOSED | PROPOSED |  | MAIL | UNIFORM | MACL | PROPOSED | PROPOSED
| FOR SIUs | CONCENTRATION | FOR COMMERCIAL | DAILY | MACL FOR |  | FOR SIUs | CONCENTRATION | FOR COMMERCIAL | MONTHLY AVERAGE | MACL FOR
POLLUTANT | LBS/DAY | FOR SIUs (MG/L) | USERS (LBS/DAY) | MAX LIMIT | COMMERCIAL USERS | POLLUTANT | LBS/DAY | FOR SIUs (MG/L) | USERS (LBS/DAY) | LIMIT | COMMERCIAL USERS | POLLUTANT
ARSENIC | Enter a % in Column P | Enter a % in Column P | #VALUE! |  |  | ARSENIC | Enter a % in Column N | Enter a % in Column N | #VALUE! |  |  | ARSENIC
CADMIUM | 0.17539 | 0.023434 | 0.70156 |  |  | CADMIUM | 0.14111 | 0.018854 | 0.32926 |  |  | CADMIUM
CHROMIUM - TOTAL | 25.2564 | 3.3745 | 51.2782 |  |  | CHROMIUM - TOTAL | 2.8148 | 0.37608 | 11.259 |  |  | CHROMIUM - TOTAL
CHROMIUM (III) | Dom or Comm Data Missing | Dom or Comm Data Missing | Dom or Comm Data Missing |  |  | CHROMIUM (III) | Dom or Comm Data Missing | Dom or Comm Data Missing | Dom or Comm Data Missing |  |  | CHROMIUM (III)
CHROMIUM (VI) | 0.33714 | 0.045046 | 1.9105 |  |  | CHROMIUM (VI) | 0.29348 | 0.039213 | 1.4329 |  |  | CHROMIUM (VI)
COPPER | 0.37654 | 0.05031 | 1.1296 |  |  | COPPER | 0.16765 | 0.0224 | 0.5944 |  |  | COPPER
LEAD | 0.47759 | 0.063811 | 4.2983 |  |  | LEAD | 0.47713 | 0.06375 | 2.7037 |  |  | LEAD
MERCURY | 0 Discharge | 0 Discharge | 0 Discharge |  |  | MERCURY | 0 Discharge | 0 Discharge | 0 Discharge |  |  | MERCURY
MOLYBDENUM | No Criteria | No Criteria | No Criteria |  |  | MOLYBDENUM | 0.29004 | 0.038753 | 1.1602 |  |  | MOLYBDENUM
NICKEL | 72.07 | 9.6294 | 255.521 |  |  | NICKEL | 1.5485 | 0.2069 | 6.1942 |  |  | NICKEL
SELENIUM | 0 Discharge | 0 Discharge | 0 Discharge |  |  | SELENIUM | 0 Discharge | 0 Discharge | 0 Discharge |  |  | SELENIUM
SILVER | 0.26746 | 0.035736 | 1.5156 |  |  | SILVER | 0.09566 | 0.012781 | 0.21292 |  |  | SILVER
ZINC | 3.0299 | 0.40482 | 17.1692 |  |  | ZINC | 7.8627 | 1.0505 | 31.4509 |  |  | ZINC